| Section 5(i) | The design of the Accommodation, the statutory submissions including the application of all requisite licenses for the execution of the Works and for operating the Accommodation, procurement of materials and lead time, and the execution and completion of the Works, all in accordance with the Agreement (including the Construction Schedule and all Schedules thereto) and all Applicable Laws (as defined in clause 1.1. of the Agreement) (collectively the “Works Stage”), including the following: |
| --- | --- |
| Section 5(i)(c) | Layout proposal and configurations for the students’ and the Pastoral Team’s (as defined in the Agreement) bedrooms, other rooms, and facilities in the Accommodation. |
| Section 5(i)(c) | 3 – BS Design |

- BS Design

The design proposal is based on the proposed building plan and sub-sequence design coordination.  The following building services installations are included in this proposal: -

- Air conditioning and mechanical ventilation system;

- Electrical supply and distribution systems, lighting, power, lightning protection, earthing system, security and extra-low voltage system;

- Plumbing and drainage systems;

- Fire Services Systems;

- Lift installation;

- Measures for Energy Efficiency & Green Features.

- BS Design Consideration

The design of building services Installations will be carried out in full coordination with the architectural plans, structural design, and other specialist system designs.  Disposition of various services and plant rooms will be carefully evaluated and coordinated with the architectural planning. The following design philosophy will be considered: -

- Employer's requirement / specification

- Statutory requirement

- Energy efficient

- Cost effectiveness

- Maintainability

- Air Conditioning and Mechanical Ventilation System

    - Design Standards, Guides and Codes of Practice

- The system design will be in compliance with the statutory requirements and code of practice established by relevant authorities and utility companies, including the following: -

- Buildings Department - Building Regulations;

- Fire Services Department - Codes of Practice (Minimum Fire Services Installations and Equipment) and current requirement including latest F.S.D. Circular Letter;

- CIBSE Guide;

- ASHRAE Handbooks and Standards; and

- Building Energy Efficiency Ordinance - Code of Practice for Energy Efficiency of Building Services Installation.

    - Design Criteria

- The design criteria detailed below form basis of the design of the ventilation and air conditioning installations and associated calculation: -

- Outdoor Design Criteria

Summer:

Dry Bulb Temperature	:	35.0oC

Wet Bulb Temperature	:	29.0oC

Winter:

Dry Bulb Temperature	:	7.0oC

- Indoor Design Conditions

| Location | Summer |  | Assumed Occupancy | Fresh Air Rate | Lighting & Electrical Load |
| --- | --- | --- | --- | --- | --- |
|  | Temp. (°C) | RH (%) | (m2/p) | (l/s/p) | (W/m2) |
| Hostel Room | 25.0 | - | No. of bed | - | 25 |
| Functional Room | 25.0 | - | 3 | 10.0 | 25 |
| Study / Meeting Room | 25.0 | - | 4p / room | 10.0 | 25 |
| Main Lobby | 25.0 | - | 10 | - | 15 |

- Ventilation Design Parameters

| Location |  | Ventilation Rate (Air Change Per Hour) |
| --- | --- | --- |
| Toilets (1) (2) |  | 10 |
| Plant Room |  | Min. 6 air change per hour, and according to the requirement of equipment and to maintain the air temperature below 40oC. |
| Pantry |  | 10 |
| Laundry |  | 10 |

Remark:

- As per APP-98 (PNAP 219), mechanical ventilation of min. 5 ACH to be required for internal domestic bathrooms.  Permanent ventilation to the ‘open air’, the ‘external air or with another room which provided with a window meeting the area requirement for the combined windows having a minimum size of 1/20 of the floor area of the room to be required.

- As per ADM-2 (PNAP30), mechanical ventilation of min. 10 ACH fresh air to be required for internal non-domestic toilets.

- As per APP-35 (PNAP98), mechanical ventilation and air purifying facilities to be provided for MRC, RS&MRR/MRC.  Where there is no particular odour problem, a mechanical fan coupled with a particulate filter at each RS&MRR/MRC may be considered, and subject to BD’s acceptance.

    - Air Conditioning System

- Split type A/C units (cooling only) with wall mounted indoor unit and remote controller will be provided for hostel rooms in general.

- Variable Refrigerant Flow (VRF) system (cooling only) with cassette indoor unit will be provided for large common areas on G/F. For individual study / meeting rooms, split type A/C units (cooling only) with cassette indoor unit will be provided for easy management and operation. Wired wall mounted controller will be installed for local control of A/C unit. Fresh air supply will be pre-treated by fresh air handling units of VRF system and supplied via insulated duct work to common areas on G/F.

- No air conditioning will be provided for typical pantry, typical lift lobby, and typical corridor.

    - Mechanical Ventilation

- Local ducted exhaust fan will be provided for bathroom of hostel in general.

- Exhaust air duct provisions will be reserved for cooking range inside pantry on typical floor. Air duct shaft will be allowed for fresh air / make up air to the pantry.

- Central ventilation system with air purifying facilities will be provided for typical refuse rooms.  Air duct shaft will be allowed for fresh air distribution and exhaust air discharge. Air purifying facilities will be installed inside the main refuse connection room according to BD’s requirement.

- Plant rooms will be provided with mechanical ventilation system. The ventilation fans inside plant room will be controlled by thermostat.

- Ducted exhaust and fresh air fans will be provided for laundry on G/F.

- A remote control panel for ventilation fans will be provided at security counter for remote control and monitoring purpose.

    - Major Material

- Condensate Drain Pipe

- Epoxy coated cast iron pipe to BS EN877.

- UPVC pipe to BS 4514 for condensate drain pipes inside and on external wall of residential blocks.

- Refrigerant Pipe

- Copper pipe to BS EN 1057 Part 2.

- Air Duct

- Galvanized steel ductwork constructed in accordance with DW/144.

- Insulation

- Flexible closed cell elastomeric insulation.

- Electrical System

    - Design Standards, Guides and Codes of Practice

- The system design will be in compliance with the statutory requirements and code of practice established by relevant authorities and utility companies, including the following:-

- Electrical Ordinance, Chapter 406 and Subsidiary Legislation;

- Fire Services Department - Codes of Practice (Minimum Fire Services Installations and Equipment) and current requirement including latest F.S.D. Circular Letter;

- Code of Practice for the Electricity (Wiring) Regulations, EMSD;

- Supply Rules of the Power Supply Company; and

- Building Energy Efficiency Ordinance – Code of Practice for Energy Efficiency of Building Services Installation.

    - H.V. Equipment and Supply System

- 2 transformer rooms will be provided for the development: 1 near Block A&B for 2 nos. 1,500kVA transformers; and 1 near Block C  for a 1,500kVA transformer.

- Details of 11kV high voltage supply cable to substations and their internal layouts shall be provided by HEC.

    - L.V. Equipment and Distribution System

- 2 sets main L.V. switchboards inside 2 main switch rooms adjacent to transformer rooms.

- The main L.V. switchboard will receive electrical power via the L.V. cable feeders from transformer and then distribute to all electrical main and sub-main system of the entire development.

    - Essential Power Supply

- Individual  emergency generator (with fuel oil storage tank underneath) will be provided for each block to supply essential power to F.S. installations (FSI equipment, essential lighting, fireman’s lift, and non-fireman’s lift homing)

- 1 set 450kVA for block A

- 1 set 250kVA for block B

- 1 set 250kVA for block C

    - Metering Arrangement

- Landlord’s services including hostel rooms to be under landlord’s meter; HEC resident’s meters for warden and senior tutor flats; and Individual HEC meter for FTNS providers inside TBE rooms.

- Digital metering provision for the feeders for each major system to identify the electricity use pattern and to comply with EMSD’s BEC requirement..

    - Lighting

- LED lighting willl be adopted and selection of lighting fitting for various areas will be selected by Architect / Interior Designer / Landscape Designer / Lighting Consultant to suit the architectural layout functionally and aesthetically.

- Lighting will be controlled by corresponding local lighting switch while lighting in public areas will be remotely controlled by programmable timer. The following table extracted from the EMSD’s Code of Practice for Energy Efficiency of Building Services Installation outlines the requirement of lighting power density (LPD) and automatic lighting control (shut off or reduce the LPD by at least 50% automatically) for various types of space of the Building: -

| - Area | - Allowable LPD - (W/m2) | - Automatic Lighting Control |
| --- | --- | --- |
| - Hostel Room | - 6.1 | - Not applicable |
| - Pantry | - 8.5 | - Occupancy Sensor + local on/off |
| - Gymnasium Room | - 9.5 | - Programmable timer + local on/off |
| - Study Room | - 9.1 | - Programmable timer + local on/off |
| - Meeting Room | - 10.6 | - Programmable timer + local on/off |
| - Lift Lobby | - 7.5 | - Programmable timer |
| - Internal Corridor | - 6.0 | - Programmable timer |

- Lighting for hostel rooms and common areas will be controlled by corresponding local lighting switch. For common areas with fenestration on exterior wall or overhead skylight, additional photo sensor will be provided for control.

- Lighting for plant rooms will be controlled by corresponding local lighting switch. Lighting in staircase will be 24-hrs operated.

- Lighting for outdoor pedestrian, walkway, traffic road and landscape area will be controlled by programmable timer and photo sensor.

    - Earthing System

- Earthing system will comprise of earthing terminal, copper down conductor, copper electrode driven into ground, earthing clamp and earth pit of appropriate size. The installation will be complied with the power company’s requirements and the regulations.

- Equipotential bonding will provided for all exposed or extraneous metal parts of the building structure under the I.E.E. Wiring Regulations and the Electricity (Wiring) Regulations promulgated under the latest Hong Kong Electricity Ordinance (Cap. 406).

    - Lightning Protection System

- Early Streamer Emission (ESE) lightning protection system will be provided to protect the development against lightning strikes.  A specialized ESE air terminal connects to copper tapes (down conductors) down to lightning pits to complete lightning protection coverage.

    - Cable Containment for Telephone Facilities

- Trunking and conduit provisions will be allowed for the telephone & data systems. Space  in TBE room and telephone / ELV duct will be reserved to accommodate future facilities by Telecommunication services providers.

- The services providers will provide their main lead-in cables and terminate inside the T.B.E. room.  Telephone cables from the local distribution board will be connected and distributed to telephone outlet points.  All these telephone cables will be supplied and installed by the telecommunication services providers.

    - Extra-low Voltage (ELV) Systems

- The following ELV systems are required according to the ER / as per the BD requirement:-

- CCTV System

A completed colour CCTV surveillance system is installed to enable and real time easy monitoring of the development by the management. CCTV cameras will be located at the following locations to give a general surveillance: -

      - Tower areas including Main Lift lobby (G/F); Typical lift lobby and corridor; Inside lift car; Temporary Refuge Spaces

      - Outdoor Area adjacent to tower

CCTV cameras with pan / tilt / zoom of fixed focus feature will be selected according to environmental requirement. All images will be transmitted and recorded down by Network Video Recorder (NVR) capable to store 24hrs x 14 days data for all cameras in the highest resolution at the caretaker’s counter.  All images will also be displayed with multi-screen of color monitor to give easy monitoring. Digital type video controller will be selected.

- CABD System

CABD system will be provided for Warden’s flat, Senior Tutor’s flat and common area of each floor and broadcasting of television programs. The system will consist of HDTV channels from Digital Terrestrial Television (DTT) signals.

Proposed location of antenna will be on roof of tower that can be access during maintenance and provide the best reception of TV signal.

- Door Access Control and Monitoring System

Access Control system will be designed by I.T. specialists. Provisions of power supply and cable containment to head-end equipment, control devices, electric locks, smart card readers, by-pass switch, etc. will be allowed. The devices for access control will be provided at:

      - Entrance gates on G/F lift lobby of each tower

      - Hostel rooms

Door monitoring system with door contacts will be proposed to monitor all exit doors at various floors, so that if any of these doors being opened during the ‘SECURE’ mode, caretaker’s counter of that tower is notified via the monitoring panel.

- Octopus Card Payment System for Laundry and Hostel A/C

Octopus card payment system will be designed by I.T. specialists. Provisions of power supply and cable containment to head-end equipment, network switches, control devices, energy metering facilities, Octopus card kiosk on G/F main lobby of each tower, etc. will be allowed.

- Wired LAN and WiFi System

Wired LAN and WiFi system will be designed by  I.T. specialists. Provisions of power supply and cable containment for Cat6  / fiber cabling to head-end equipment, network switches, public WiFi access points, data point for modem and WiFi router inside hostel rooms, etc. will be allowed.

- Intercom System

In accordance with the CoP for Fire Safety in Building 2011, a direct intercom system will be provided to every Temporary Refuge Space (TRS) for communication with Office Accommodation for Watchman & Caretakers or caretaker’s counter.

- Emergency Call Bell and Alarm System

An emergency call bell with waterproof push button for activating alarm bell will be provided for each free access rooms / toilet, according to the requirement of “Barrier Free Access 2008” of the BD.  The call annunciation will be provided by a call bell outside the toilet or buzzer in the caretaker counter.

- Fire Services System

    - Design Standards, Guides and Codes of Practice

- The system design will be in compliance with the statutory requirements and code of practice established by relevant authorities and utility companies, including the following: -

- Buildings Department - Building Regulations, Code of Practice for Fire Safety in Buildings 2011, and Design Manual - Barriers Free Access 2008;

- Fire Services Department - Codes of Practice for Minimum Fire Service Installations and Equipment (April 2022 Edition) and current requirement including latest FSD Circular Letters;

- Loss Prevention Council - LPC Rules for Automatic Sprinkler Installations Incorporating BS EN 12845:2015;

- British Standard – Fire Detection and Fire Alarm System for Building – Part 1: Code of Practice for System Design, Installation, Commissioning and Maintenance (BS 5839-1:2002 + A2:2008);

- Water Supplies Department - Waterworks Regulations (Cap. 102A) and Hong Kong Waterworks Standard Requirements for Plumbing Installation in Buildings; and

- Electrical and Mechanical Services Department - Code of Practice for the Electricity (Wiring) Regulations.

    - Street Fire Hydrant System

- A street fire hydrant system will be provided along the internal EVA of the site, with spacing between fire hydrants at maximum 100 meters of the roadway.

- Water supply will be connected to respective 245m3 street fire hydrant water tanks.  At the street fire hydrant water tank, the water will be supply to street fire hydrant pump at street fire hydrant pump rooms, and subsequently transfer to street fire hydrant(s) in order to achieve to achieve design flow rate and pressure as stated in Codes of Practices of FSD.

    - Fire Hydrant / Hose Reel System

- The fire hydrant/hose reel system will be designed as wet pipe system and thus charged with water to the required pressure at all time.  Hose reel system enables first hand fire fighting by building occupants whereas fire hydrant system is designed for firemen’s use.  Fire hydrant and hose reel will be located at each floor in order to provide full coverage of the entire floor area as the FSD requirements.

- 1 set of fire hydrant and hose reel system will be provided for each tower, and the correspondence capacity of F.S. water tank is 27 m3. From F.S. water tank, the water will be supplied to fixed fire pump at F.S. pump room and subsequently transferred the water to fire hydrants and hose reels at the respective floor to maintain the flow and the pressure requirement as per the FSD requirements as stated in Code of Practice.

- One F.S. Inlet will be provided to each staircases.  As the static pressure at the hydrant outlet is greater than 850kPa, self-contained pressure reducing hydrant will be provided.

    - Automatic Sprinkler System

- 1 set of automatic sprinkler system will be provided for each tower to detect a fire and extinguish it with water in its early stages or control the fire for subsequent extinguishment by firemen.

- The system will be designed in accordance with the LPC Rules for Automatic Sprinkler Installations Incorporating BS EN 12845:2003 as wet pipe system so that the system pipework is charged with water under its operational pressure and in event of sprinkler head operation the water is discharged immediately.

- The classification of hazard group of automatic sprinkler system will be designed as Ordinary Hazard Group 1(OH1) in accordance with  LPC Rules. The capacity of sprinkler water tank is 54m3 and based on 2/3 of full capacity of sprinkler water tank plus individual direct telephone line from each tower to Services Provider’s Computerized Fire Alarm Transmission System.

- At the sprinkler water tank, the water will be supply to sprinkler pump at sprinkler pump rooms, and subsequently transfer to sprinkler systems to achieve minimum pressure and flow requirement as stated in LPC Rules.

- Sprinkler system will be provided to cover entire building, except plant rooms, services duct, electrical meter room, water meter cabinet, cable trenches, and subject to exemption approval from FSD.

    - Automatic Fire Detection and Fire Alarm System

- 1 set of automatic fire detection and fire alarm system will be provided for each tower for protection in order to alter building occupants to a fire and start a timely evacuation of the building.

- An addressable system will be installed.  They use detectors which constantly relay information on their operating condition to the control.  This type of information will allow the control panel to determine if a particular detector is being subjected to an abnormally high ambient level of smoke in normal use.  Main fire control panel will be provided and located at F.S. control room at with direct telephone line to Hong Kong Fire Control Centre.  It mainly integrated all fire detection and fire alarm initiation signals of podium floors and residential floors.

- Automatic fire detection systems, which consist of smoke and heat detectors, are designed to raise the alarm whether or not personnel are presents at the time, thus giving early warning of fire incident.  The system will be provided for the following areas in accordance with FSD’s requirements: -

- Smoke detectors integrated with proprietary made sounder base for  hostel rooms;

- Smoke detectors for entire floor with sleeping accommodation except toilets, bathrooms, staircases which are covered by sprinkler system;

- Heater detectors for new M&E plant rooms;

- All areas are not protected by automatic sprinkler system;

- Generally, rate of rise temperature type heat detectors will be adopted for the M/E plant rooms to minimize the false/unwanted alarm of the system. For actuation of others F.S. system, photoelectric type smoke detectors will be provided.

- Manual fire alarm system consisting addressable type normal break glass units and alarm bell will be provided at each hose reel points, each storey exits and adjacent to all staircase exits to open air on G/F.

    - Visual Fire Alarm System

- Visual Fire Alarm System (VFA System) in additional to audio warning devices, i.e. alarm bells, will be provided to form part of the fire alarm system in accordance with Design Manual: Barriers Free Access 2008 to suit the new architectural layout plans of the A&A works areas

    - Portable Fire Extinguisher and Equipment

- Portable fire fighting equipment will be provided to the building’s requirements and to facilitate immediate first aid fire fighting purpose.  In general, the type of portable fire fighting equipment will be chosen, based upon the fuel or fuels present in various portions of the facility, as follows: -

- 4.5kg CO2 fire extinguishers for M&E plant rooms;

- 9 litres water/CO2 fire extinguishers for refuse storage chamber;

- 4.5kg CO2 fire extinguishers for pantry.

    - Ventilation / Air-conditioning Control System

- “Method C” override control will be adopted.  This override control will be arranged to completely shut down the related fans in the building and the actuation will be provided by the fire alarm system.

- Plumbing and Drainage System

    - Design Standards, Guides and Codes of Practice

- The system design will be in compliance with the statutory requirements and code of practice established by relevant authorities and utility companies, including the following: -

- Building Department - Building Regulations and Practice Notes for Authority Person.

- Office of the Water Authority - Waterworks Regulations

- Drainage Services Department;

- Highways Department;

- Environmental Protection Department;

- The Institute of Plumbing - Plumbing Engineering Services Design Guide;

- CIBSE Guide; and

- Building Energy Efficiency Ordinance - Code of Practice for Energy Efficiency of Building Services Installation.

    - Design Criteria and Basic Assumption

- The water storage capacity will be provided in accordance with the Waterworks Regulation as shown below: -

Flushing Water		-	40 litres / water closet

Fresh Water 	-	45 litres / signle room

-	45 litrers / point of general ablutions

- System pressure of various water supply systems will be designed to operate within the following pressure ranges:-

For general ablutions	:	2.0 bar to 6.0 bar

For flushing		:	1.0 bar to 6.0 bar

- Sanitary fitments should be selected by Architect / Interior Designer subject to client’s approval.

- The design of drainage sump pump system will be limited to a maximum of 12 cycle of start / stop per hours, if necessary.

    - Potable Water Supply System

- Fresh water will be taken from the fresh water supply main to fiber glass sump tank at G/F and transferred to fiber glass storage tank on roof by upfeed water pumping system.  The fresh water will be supplied to building by variable speed booster pumping system (high zone), and by gravity (low zone).

- “Twin Water Tank” will be allowed to minimize inconvenience to building occupancies due to temporary suspension of water supply during periodic cleansing of water tanks.

- Metering arrangements for various applications: -

- 1 nos. water meters for general ablutions including hostel rooms;

- 1 no. water meter for warden’s flat;

- 1 no. water meter for senior tutor’s flats;

- 1 no. water meter for cleansing water; and

- 1 no. water meter for irrigation water.

- A remote indication panel for water tank and pumping system will be provided at G/F security counter for monitoring purpose.

    - Flushing Water Supply System

- Flushing Water Supply would be similar to potable water supply system.

    - Hot Water Supply System

- Electrical water heater for hot water supply as below: -

| - Hostel bathroom | - One 3kW, 38L Storage type electric water heater |
| --- | --- |
| - Sink in pantry | - One 3kW Instantaneous type electric water heater |
| - warden’s flat / - tutor’s flats | - One 21kW Instantaneous type electric water heater for bathroom plus one 6kW Instantaneous type electric water heater for kitchen sink |

    - Cleansing Water System

- Cleansing water supply for main refuse room and typical refuse room will be fed from fresh water supply main to fiber glass cleansing water break tank at G/F.  Cleansing water will be supplied by pneumatic pumping system to maintain the operating water pressure.

    - Irrigation Water System

- Irrigation water supply will be fed from fresh water supply main to fiber glass irrigation water tank at G/F. Water will be supplied by pneumatic pumping system to maintain the operating water pressure.

    - Soil & Waste Water Disposal System

- Existing dia.150mm S&W main discharge pipe from terminal manhole of the site is connecting to the existing government manhole. There is intention to remain the existing main discharge pipe, subject to approval from the BD and the DSD.

- Gravity discharge of S&W water will be used generally for the development.

- Combined soil and waste fully vented one pipe system will be adopted for the building. Internal / external drainage stacks, where appropriate, will be allowed for bathrooms of hostel. Cross-vent will be provided for every 3 stories of soil and waste stack.  The stack will be individually trapped and connected separately via gully trap to the manhole system to avoid back flow of smell. Separate down stacks will be allowed for the lower floors.

- Floor drain inside bathroom will be provided with “re-filling pipe” which automatically fills the trap of floor drain using water by-passed from bathroom basin.

- Dry sump pits will be allowed at new lift pit, if any.

    - Storm Water Disposal System

- Existing dia.350mm storm water main discharge pipe from terminal manhole of the site is connecting to the existing government manhole. There is intention to remain the existing main discharge pipe as there is no change of existing catchment areas.

    - Major Material

- Potable Water Pipe

- Plastic covered copper pipe to BS EN 1057 for size up to 65mm dia.

- Ductile iron pipe to BS 4772 Class K12 for size 80mm dia. and above.

- Cleansing Water Pipe

- Plastic covered copper pipe to BS EN 1057 for size up to 65mm dia.

- Flushing Water Pipe

- uPVC pipe to BS 3505 Class E for size up to 65mm dia.

- Ductile iron pipe to BS 4772 Class K12 for size 80mm dia. and above.

- Soil, Waste and Vent Pipe

- uPVC pipe to BS 4514 for above ground service for external only.

- Epoxy coated cast iron pipe to BS EN877 for above ground service of internal pipe duct.

- Cast iron pipe to BS 437 and BS1211 for underground service.

- Storm Water Pipe

- uPVC pipe to BS 4514 for above ground service of the residential block for external only.

- Epoxy coated cast iron pipe to BS EN877 for above ground service of internal pipe duct.

- Cast iron pipe to BS 437/BS 4662 for underground service.

- Vertical transportation system

    - Design Criteria and Assumption

- The performance in terms of handling capacity and waiting interval are calculated according to international codes.

- Reference Guide - “CIBSE Guide D : 2020 - Transportation Systems in Buildings” is taken as the reference for system design

- Building Type - Residential Building

- Percentage 5-Mintue Handling Capacity - According to Table 3.16 of CIBSE Guide D : 2020, the minimum arrival rate (percentage in 5-min handling capacity) shall be 6% for standard design criteria.

- Waiting Interval - According to Table 3.16 of CIBSE Guide D : 2020, the maximum up-peak interval shall be 60 seconds for standard design criteria

    - Lift Configuration

- There are 2 nos. existing Lifts. The existing 400kg passenger lift  will be demolished while the existing 680kg firemen’s lift will be replaced by new to suit architectural layout. A new 900kg lift will be installed as per architectural design.

- Environmental Issues

    - Energy Efficiency

- Energy use can be improved by implementing energy saving measures and design.  In particular, the following energy efficient measures and design will be proposed in this project: -

- Use of high efficiency equipment:-

- Use of frequency inverter control for water supply pumping system to provide variable supply flow according to the actual water demand.  Pump energy can be saved.

- Use of high efficiency motor for water pumps.

- Use of high COP or Energy Label Grade 1/2 air conditioners

- Control of systems:-

- Thermostat at M&E plant room for ventilation fan control.

- Zoning control of lighting system. All lighting systems for illumination purpose will be divided into different zones for energy saving purpose to tailor suit seasonal daylight requirement / actual need, on top of emergency lighting.

- Motion detection sensor for lighting control.

- Use of LED lamp as lamp source to increase the lumen output and hence energy saving achieved.

    - “Green” Building System

- Advance M&E systems with “Green” feature makes contribution to the environment.  The following section introduces some for client’s consideration.

- Reserving water use

- Selection of the water using appliances / apparatus would be considered by Client / Architect with the following features:-

- Use of water-saving basin mixer

- Usage of dual flush water cistern

- Use of Class 1 water efficiency label mixer

- Ozone depletion

- Use of refrigerants with zero ozone depletion potential, such as R410A and R32, in air-conditioning units and other refrigeration systems, together with materials free from CFCs and HCFCs

- Provision for charging station of the electric car

- Electric car is now become the trend in the world. Electric car emit less roadside emission and more energy efficient than fossil-fuel car.  Provision of charging station allow people with more convenient charging facility.

- Provision of Photovoltaic (PV) system

- A photovoltaic (PV) system consists of solar panels installed on the tower roof, converting sunlight into electricity. The generated power is fed through inverters to supply building loads or connect to the grid. This clean energy solution reduces reliance on fossil fuels and supports sustainable building operations

- Apprendix

    - Cooling Load Estimation

    - Electrical Loading Estimation

    - Estimation of Water Tank Capacity

    - Lift Traffic Estimation

- Conceptual Design Drawings

- (Refer to drawing list)